## Sheet1
COIL & INPUT STATUS MODBUS FUNCTION 1 = FUNCTION 2 read I/O pin
0 + N | I/O N | where N is 0..9 (I/O 0 to I/O 9)
READ HOLDING REGISTER FUNCTION 3
0 + N | R/C servo or PWM value of I/O N
160 | Read slave modbus address
250 | Read software version
251 | Read software ID number
256 + N (0x100+N) | Read I/O N configuration
READ INPUT REGISTER MODBUS FUNCTION 4
N*16 (N * 0x10) | Read I/O N sensor Data. (Data length is configuration mode specific)
4096 (0x1000) | Read Ref 2.048V A/D value. This use VCC for reference
4097 (0x1001) | Read build-in diode temperature sensor
Sensor Data is configuration specific
A/D | 1 WORD
INPUT/OUTPUT | 1 WORD (0=OFF 1=ON)
CAP SENSE | 2 WORD | one single DWORD
DHT11&DHT22 | 3 WORD | WORD0 => 0xFFFF = no sensor found, 0 = ok WORD1=> humidity WORD2 => temperature
DS18B20 | 2 WORD | WORD0 => 0xFFFF = no sensor found, 0 = ok WORD1=> temperature (short value * 0.0625)
COUNTER | 3 WORD | WORD0 & WORD1 => DWORD totaliser WORD2 => pulse per second
*** you need to send the request with exactly the number of register for the specific function.
FORCE SINGLE COIL MODBUS FUNCTION 5
N | Set I/O N bit output
PRESET SINGLE REGISTER MODBUS FUNCTION 6
N | Set R/C SERVO, PWM output or CLEAR COUNTER (configuration mode specific)
160 | Set Modbus slave address. Need to be unlock first by writing 0x5678 to single register 0x1ff
256+N (0x100+N) | Set I/O N configuration. Need to be unlock with register 0x1ff
511 (0x1FF) | set the value to 0x5678 will unlock the system to change modbus slave address
0xAA55 | Writing 0x1234 force a reset.
N.B. To change Modbus address Or I/O configuration you need to remove the lock